## Slide 1
Full-scope simulation of grid-connected microgrids
dr. Attila KOVÁCS
Astron Informatics Ltd. Hungary
Motivation
spreading of renewable generation, storage technology
need for simulation tool for microgrid modelling, supporting design and future operation
main focus on investigating operation modes, controlling schemas
Method/Approach
distribution network training simulator (NTS) completed with new simulation models as:
  renewable generation & consuming units
  storage unit
  microgrid control system (regulator)
quasy-stationary flow- and detailed discrete event modelling
Objects of investigation, the modelled network
separable low voltage network
BLACK and GREEN busbars for free configuration of the loads
internal renewables connected to the GREEN busbar
Experimental setup, simulator architecture
per-phase, special load-flow
single-node effective power-frequency model
simulator engine for controlling model computations
Study Committee C6
Active distribution systems and distributed energy resources
Paper C6_304_2018
„GREEN” busbar
G
=
~
=
~
=
~
=
~
+
-
M
Regulator
Renewables
Consumers
Biogas motor
Solar panel
Water turb.
Wind turb.
Battery
Car charger
Paddock
light
Watering pump
Offices
Visitor
center
20 kV Public electric network
„BLACK” busbar
0,4 kV
G
Generator
INPUT
OUTPUT
Solar panels
INPUT
OUTPUT
Water turb.
INPUT
OUTPUT
Wind turb.
INPUT
OUTPUT
Battery
INPUT
OUTPUT
Consumers
INPUT
OUTPUT
Simulation time
Signal distribution
Conditional Events
Scenarios
Simulator functions
Device models
Load-flow calculation
Simulator engine
P-f
modelling
Electrical calc. func.

## Slide 2
Full-scope simulation of grid-connected microgrids
(continued)
Study Committee C6
Active distribution systems and distributed energy resources
Paper C6_304_2018
Model of renewables
handling multiplied set-point sources
primary energy source (wind, sun, water) transformation
ramping up/down curves
E
P
Primary energy
conversion
Ramping up/down
t
P
Current Output Power
Psetpoint multiplexer
Psetpoint
E
P
Esetpoint multiplexer
GUI
Cond. event
Regulator
Schedule
GUI
Cond. event
Regulator
Schedule
Primary Energy set-point source
Electrical power set-point source
P
Start
P_balance = P_cons - P_gen
PG<PC ?
Ppublic netw.
P <=Pmax
Batt level > Min ?
P_balance > P_discarge_max ?
Batt. Level < Non. Critical consumers
Island mode
PG>PC
case
Battery discharge with max power
Battery discharge with P_balance power
Switching off non critical consumers
Y
Y
Y
Y
Y
N
N
N
N
N
Start
P_balance = P_cons - P_gen
PG>PC ?
Ppublic netw.
P <=Pmax
Batt level > Level of switching on noncritical consumer?
P_balance > P_charge_max ?
Island mode
PG<PC
case
Battery charge with max power
Battery charge with P_balance power
Y
Y
Y
Y
N
N
N
N
Are there on switchable critical consumer?
Batt level exceeds upper limit?
Switching on non critical consumers
Y
N
Y
N
Consumption > Generation
Consumption < Generation
Regulator algorithm
parallel (coupled) network operation mode
maximal renewal energy utilization
managing lack/surplus of renewable generation
controlling storage unit, switching in/off non-critical consumers

## Slide 3
Full-scope simulation of grid-connected microgrids
(continued)
Study Committee C6
Active distribution systems and distributed energy resources
Paper C6_304_2018
Test case 1
parallel network mode, maximal utilization of renewable energy
sunny summer day, slight wind
at night street light was switched on and in office buildings only the refrigerators and security systems consumed energy
the battery has been half charged at midnight
the watering pumps of high power were switched on in early morning and late afternoon
the biogas motor was in operation to ensure enough energy for watering in the morning
Conclusion
FMS is an appropriate tool for investigating:
  future microgrid configurations/architectures
  operational modes, controlling schemas
further development: simulation large number of microgrids in order to study distribution network/power system control impacts
Test case 2
like Test case 1 but the biogas motor was OUT, so the morning watering was cancelled by microgrid controller as the battery level reached „non critical consumer switching off” limit